
[image: image1.jpg]


[image: image2.png][image: image3.png]satrery
current

Ammeter Voltmeter
(connecte in series ) (Connected n paralel)



[image: image4.jpg]\'or EDUCATION

DEPARTMENT



[image: image5.jpg]


[image: image6.jpg]


[image: image7.jpg]


[image: image8.jpg]



[image: image9.png]



TABLE OF CONTENTS

Page

How to Use this Module
i
Introduction
ii
Technical Terms
iii
Learning Outcome 1: Perform preliminary activities for commissioning
· Learning Experiences/Activities
2
· Information Sheet 1.1
2
· Self-Check 1.1
7
Learning Outcome 2: Ensure normal operability of electrical system
· Learning Experiences/Activities
9
· Operation Sheet 2.1
9
· Operation Sheet 2.2
11
· Operation Sheet 2.3
12
· Operation Sheet 2.4
13
· Operation Sheet 2.5
15
· Operation Sheet 2.6
17
Learning Outcome 3: Finalize commissioning activities
· Learning Experiences/Activities
20
· Information Sheet 3.1
20
· Self-Check 3.1
21
· Activity Sheet 3.1
22
Assessment Plan
23
Observation Checklist
24
Observation and Questioning Checklist
25
Demonstration
26
Written Report
27
Performance Test
28
Answer Key 1.1
29
Answer Key 3.1
29
HOW TO USE THIS MODULE

Welcome to the Module “Commissioning Electrical System”. This module contains training materials and activities for you to complete.

The unit of competency “Commission Installed Electrical Systems” contains the knowledge, skills and attitudes required for Building Wiring Installation course required to obtain the National Certificate (NC) level II. 
You are required to go through a series of learning activities in order to complete each of the learning outcomes of the module. In each learning outcome there are Information Sheets, Job Sheets, Operation Sheets and Activity Sheets. Do these activities on your own and answer the Self-Check at the end of each learning activity.

 If you have questions, do not hesitate to ask your teacher for assistance.

Recognition of Prior Learning (RPL)

You may already have some basic knowledge and skills covered in this module.  If you can demonstrate competence to your teacher in a particular skill, talk to your teacher so you do not have to undergo the same training again. If you have a qualification or Certificate of Competency from previous trainings show it to him/her. If the skills you acquired are consistent with and relevant to this module, they become part of the evidence. You can present these for RPL. If you are not sure about your competence skills, discuss this with your teacher.

After completing this module, ask your teacher to assess your competence. Result of your assessment will be recorded in your competency profile. All the learning activities are designed for you to complete at your own pace.

In this module, you will find the activities for you to complete and relevant information sheets for each learning outcome. Each learning outcome may have more than one learning activity.

This module is prepared to help you achieve the required competency in receiving and relaying information.  This will be the source of information that will enable you to acquire the knowledge and skills in Building Wiring Installation NC II independently at your own pace with minimum supervision from your teacher. 

	Program/Course:
	BUILDING WIRING INSTALLATION NC II

	Unit of Competency:
	COMMISSION INSTALLED ELECTRICAL SYSTEM

	Module Title:
	Commissioning Electrical System


INTRODUCTION:

This module contains information and suggested learning activities in the installation of wiring devices for floor and ground fault current interrupting outlets. It includes instructions and procedure on how to install and select electrical boxes.

This module consists of three (3) learning outcomes. Each learning outcome contains learning activities supported by instruction sheets.  Before you perform the instructions, read the information sheets and answer the self-check and activities provided to ascertain to yourself and your instructor that you have acquired the knowledge necessary to perform the skill portion of the particular learning outcome.

Upon completing this module, report to your instructor for assessment to check your achievement of knowledge and skills requirements of this module.  If you pass the assessment, you will be given a certificate of completion. 

SUMMARY OF LEARNING OUTCOMES

Upon completion of the module the students shall be able to:

LO1
 Perform preliminary activities for commissioning
LO2
 Ensure normal operability of electrical system
LO3   Finalize commissioning activities

ASSESSMENT CRITERIA
 

Refer to assessment criteria of learning outcomes 1-3 of this module.

PREREQUISITES

Basic and Common Competency
TECHNICAL TERMS

Amprobe's Phase Sequence and Motor Rotation Tester is used to assure used to assure proper and safe connection of the electrical equipment on three-phase systems

Amperage (Amps) is a measure of electrical current flow.
Circuit breaker or fuses is used to protect against over-current and short circuit conditions that could result in potential fire hazards and explosion.
Closed circuit is a circuit where electricity flows from an energy source to the desired endpoint of the circuit.
Commissioning is a process of verifying that building systems operate and function at a high performance level, as designed.
Commissioning Process is a quality-oriented process for achieving, verifying and documenting that the performance of the facilities, systems, and assemblies meets the defined objectives and criteria.
Ground/grounding is a conducting connection, whether intentional or accidental, by which an electric circuit or equipment is connected to the earth, or to some conducting body of relatively large extent that serves in place of the earth.
Hipot tester is an electronic device used to verify the electrical insulation in a cable, printed circuit board, electric motor, transformer or other wired assembly.
LCD refers to Liquid Crystal Display.
Multi-tester is used to measure the voltage, the resistance or the current of a circuit. It is connected in either parallel or series with the circuit depending on what to measure.
Megger is an instrument used to measure the insulation resistance of conductors or wire. It is measured in ohms or meg-ohms.
Open circuit is a circuit constructed from conductors that are separately supported by insulators.
PPE refers to Personal Protective Equipment.
Short circuit is an abnormal electrical path.
VAC refers to Voltage Alternating Current.

VDC refers to Voltage Direct Current.
Voltage (volts) is a measure of electrical potential.
	Program/Course:
	BUILDING WIRING INSTALLATION NC II

	Unit of Competency:
	commission installed electrical system

	Module Title:
	Commissioning Electrical System


Learning Outcome 1:  Perform preliminary activities for commissioning
Assessment Criteria
	1. Scope of work is confirmed to ensure clear understanding of job elements.

	2. Planning of commissioning activity is performed in line with work requirements.

	3. Materials, tools and equipment needed for commissioning are prepared according to work requirements.


References:
1. Institute of Integrated Electrical Engineers of the Philippines Incorporated. Philippine Electrical Code of 1992.
2. Max B. Fajardo Jr. & Leo R. Fajardo.  Electrical Layout and Estimate, 2nd Edition.

3. Azares, Efren F. and Recana, Cirilo B.  Practical Electricity III; Adriana Publishing: 1999.

4. Roland E. Palmquist.  Audel House Wiring, 7th Edition.

5. www.des.od.nih.gov/eWebb/…/commissioning/nih_cxguide/cxspecs/1699555k
6. www.epa.gov/rtp/new-bldg/environmental/0910updf
7. www.megger.com/au/products
8. www.omnicontrols.com/manufacturer.megger.aspx

9. www.amprove.com/manuals/PRMZ-pdf

10. www.wikihow.com/use-a-multimeter
11. www.acmehowto.com/howto/maintenance/electrical/onthevoltage.htm
	LEARNING EXPERIENCES/ACTIVITIES



	Learning Outcome 1:  Perform preliminary activities for commissioning

	Learning Activities
	Special Instructions 

	1. Read the attached Information Sheet 1.1 on:
· Scope of work

· Different work activities in commissioning

· Equipment needed for commissioning


	· You can ask the assistance of your teacher to explain topics you cannot understand.

	2. Answer Self-Check 1.1 to test your knowledge on the different work activities and scope of work in commissioning.

	

	3. Compare your answer to Answer Key 1.1.

	· 

	4. When you are ready, you can proceed to L.O.  2.


	· 


Information Sheet 1.1
different work activities needed in commissioning
INTRODUCTION

The enjoyment of opening a new building or starting up a new mechanical or electrical system can be annoying quickly if the system does not work the way manufacturer, integrator or designers intended. One way to help avoid this disappointment and subsequent costly refinements or repairs is Commissioning.
Commissioning helps ensure that the system/s will meet the needs of the owner and occupants. It also verifies that the designed system meets the owners requirements and that construction confirms to the contract documents and the system/s operate as needed.
Commissioning building usually covers air conditioning, electrical, communications, security and fire management system and   their controls.  It may also include other systems and components, particularly if they are unusual or complex.

Electrical System Commissioning
A. Work included

· Systems and equipment testing and start-up. 

· Validation of proper and thorough installation of systems and equipment 

· Equipment performance verification. 

· Functional testing of electrical systems. 

· Documentation of tests, procedures, and installations. 

· Coordination of training.
B. Scope
· Systems to be commissioned include the following:
1. Secondary Service Electrical Systems 

2. Motor Control Centers 

3. Distribution and Branch circuit panel boards 

4. Lighting Fixtures and Controls 

5. Lightning Protection Equipment and Lightning Protection Systems 

6. Equipment Monitoring 

7. Fire Alarm Equipment/Fire Alarm Equipment Monitoring System 

8. AC motors 

9. Grounding Equipment and Building Grounding System 

10. Security System 

11. Emergency Generators and Distribution System 

12. Uninterruptible Power Systems 

Along with drawings and equipment manuals, a final commissioning report is also submitted to the owner. A complete commissioning report contains:
· All record of the commissioning procedures
· Testing results
· Deficiency notices and records of the satisfactory corrections of deficiencies.

The following areas are addressed: general commissioning criteria, commissioning plan, documentation requirements, verification procedures system functional performance tests, deferred  performance tests, corrective measures, acceptance documentation, post commissioning follow-up procedures and examples of commissioning.
General system testing requirements 
The purpose of electric systems commissioning is to increase the reliability of electric power system after installation by identifying problems and providing a set of baseline values for comparison with subsequent routine tests. A procedure should be developed to include a planned approach (road map) of what should be done in order to verify the proper system installation. This procedure is the commissioning plan. Specific areas addressed in a commissioning plan include the verification of the installation of all equipment/components, interface connections between equipment and individual system, and interconnection drawings. The development of this test plan specific to each system and/or component is key to the usefulness of any maintenance program. The plan consists of: a) the schedule of when acceptance and routine tests should be performed; b) test forms to be used to record the outcome of the tests which are retained for comparison with previous and subsequent tests; and c) a listing of the required test devices. Since the results of the commissioning tests become baseline test values to compare with later tests and the results of the routine maintenance tests are compiled to identify any downward trend in performance, it is vital to the maintenance program to have accurate and complete records. To perform the testing, the plan lists all required tests in order of performance and gives a schedule for each test. The work items and schedule depend on many items including the importance and cost of the equipment, consequences of failure, age of equipment, past and future frequency of service, hours of operation, future maintenance availability, environmental conditions, and safety requirements. 
Component testing 
Commissioning requirements for the system components are typically provided with the original proposal for the procurement of the equipment. The requirements provided by the equipment manufacturer should be adhered to in addition to the recommended testing herein. Although there are many different components in any electrical system, there are some tests that are common among the equipment. Examples of the common testing procedures include the assembly check, alignment check, grounding verification, insulation resistance tests and polarization index to name a few.
Sufficient time should be allocated to define the inspections required, perform the check, and document the results. A review of the system drawings will show major pieces of equipment. Specific procedures should be developed for each test referencing the equipment to be used, drawings to be followed, and step by step procedures with readings to be recorded and forms for the results. 
System commissioning testing 
Electrical system commissioning on new projects is critical to ascertain that a system is installed properly and that it will operate as designed. The commissioning of a system encompasses the individual testing of the related components, the verification of the component interconnection against the drawings, and the functional testing of the system as a whole. An understanding of the equipment involved and the modes of operation for a system are essential to the development of the system commissioning plan. A survey of the equipment of the system and listing the equipment in order of importance and startup is the first step in developing the commissioning plan. The schedule of the tests and inspections is dependent on many aspects of the equipment such as its importance and cost, the frequency of service, hours of operation, environmental conditions, accessibility, and safety requirements. The inspection, testing, and startup plan is then developed in conjunction with this schedule with instructions and procedures for the test plan. Problems may arise during the testing of the equipment and system. In order to identify and correct these problems, troubleshooting techniques should be developed. Checking of equipment such as fuses, lights, and breakers for continuity, equipment calibration and settings, and investigating for faulty equipment or connections should be the first troubleshooting steps. For all problems, the equipment and component manuals are consulted for troubleshooting directions.
Equipment Needed in Commissioning

Multi-tester is used to measure the voltage, the resistance or the current of a circuit. It is connected in either parallel or series with the circuit depending on what to measure.
A multimeter can be a hand-held device useful for basic fault finding and field service work or a bench instrument which can measure to a very high degree of accuracy. They can be used to troubleshoot electrical problems in a wide array of industrial and household devices such as batteries, motor controls, appliances, power supplies, and wiring systems. 
	[image: image10.jpg]



	[image: image11.jpg]




	Analog Multimeter
	Digital multimeter


[image: image12.png]


Megger is an instrument used to measure the insulation resistance of conductors or wire. It is measured in ohms or meg-ohms. It is connected in parallel with the circuit.
A megger (or sometimes meggar) is often used as an alternate term for an insulation tester - a circuit tester which puts a very high voltage at a very low current across two conductors to make sure that they are properly insulated. The word is short for megohm-meter
[image: image13.png]


High potential tester is an electronic device used to verify the electrical insulation in a cable, printed circuit board, electric motor, transformer or other wired assembly. A hipot tester is used to perform a high potential test. Generally a hipot tester consists of:
· A source of high voltage, 

· A current meter, 

· A switching matrix used to connect the high voltage source and the current meter to all of the contact points in a cable. 
In addition to these parts a hipot tester may also have a microcontroller and a display to automate the testing process and display the testing results.
A hipot tester can be very similar to a cable tester and often the two are combined into a single device.

A hipot tester is used to verify the circuits that should be insulated. It is done by applying a high voltage between the circuits and making sure no current flows.
[image: image14.jpg]


In a typical wired assembly, a hipot test should connect all circuits in common to ground. Then, one by one the tester will disconnect a given circuit from ground and connect that circuit to high voltage. The current that flows is monitored to verify that it is low enough.

Phase sequence tester - is two measurement devices in one unit that provides three functions - phase sequence identification, open phase condition and motor rotation indication. Amprobe's Phase Sequence and Motor Rotation Tester is used to assure proper and safe connection of the electrical equipment on three-phase systems.
Phase sequence testing is crucial for some of the three-phase loads, whenever they need to be connected to the electrical system. Improper connection of three-phase motors may lead to reverse rotation, and as a result it may damage equipment powered by a motor. 
Note. In this module, the focus of the commissioning process lies on the following:      

· Insulation resistance

· Earth resistance test
· Phase sequence test

SELF-CHECK 1.1
A.  Direction: Enumerate the following:
1-12.   
Scope of commissioning electrical system

13-18.
Work included in commissioning process

B.  Direction: Identify the word or words being referred to by the statement. Write the answer on your answer sheet.
	
	1. It is a device used to verify the electrical insulation in a cable, printed circuit board, electric motor, transformer or other wired assembly.

	
	2. 

	
	3. It is used to assure proper and safe connection of the electrical equipment on three-phase systems.

	
	4. 

	
	5. It is an instrument used to measure the insulation resistance of conductors or wire.

	
	6. 

	
	7. It is used to measure either, the voltage, the resistance or the current of a circuit.

	
	8. 


	Program/Course:
	BUILDING WIRING INSTALLATION NC II

	Unit of Competency:
	commission installed electrical system

	Module Title:
	Commissioning Electrical System


Learning Outcome 2:  Ensure normal operability of electrical system
Assessment Criteria

	1. Continuity of circuit is measured following prescribed procedure.

	2. Insulation resistance is performed in following prescribed procedure.

	3. Supply voltage is measured following prescribed procedure.

	4. Earth resistance test is performed following prescribed procedure.

	5. Phase sequence testing is performed following prescribed procedure.


References:
1. Institute of Integrated Electrical Engineers of the Philippines Incorporated. Philippine Electrical Code of 1992.
2. Max B. Fajardo Jr. & Leo R. Fajardo.  Electrical Layout and Estimate, 2nd Edition.

3. Azares, Efren F. and Recana, Cirilo B.  Practical Electricity III; Adriana Publishing: 1999.

4. Roland E. Palmquist.  Audel House Wiring, 7th Edition.

5. www.des.od.nih.gov/eWebb/…/commissioning/nih_cxguide/cxspecs/1699555k
6. www.epa.gov/rtp/new-bldg/environmental/0910updf
7. www.megger.com/au/products
8. www.omnicontrols.com/manufacturer.megger.aspx

9. www.amprove.com/manuals/PRMZ-pdf

10. www.wikihow.com/use-a-multimeter

11. www.acmehowto.com/howto/maintenance/electrical/onthevoltage.htm
	LEARNING EXPERIENCES/ACTIVITIES



	Learning Outcome 2:  Ensure normal operability of electrical system

	Learning Activities
	Special Instructions 

	1. Perform Operation Sheet 2.1 on testing the continuity of a circuit.


	· You can ask the assistance of your teacher in case problems arise.

	2. Perform Operation Sheet 2.2 on tracing short circuit or overload.
	

	3. Perform Operation Sheet 2.3 on testing the insulation resistance of a conductor.
	

	4. Perform Operation Sheet 2.4 on measuring the supply voltage of an electrical circuit.
	

	5. Perform Operation Sheet 2.5 on testing earth resistance.
	· You can ask the assistance of your teacher in case problems arise.

	6. Perform Operation Sheet 2.6 on testing phase sequence of a component.
	


operation Sheet 2.1
testing the continuity of a circuit
Tools and Equipment

· Laboratory circuit board
· Multitester
· Screwdriver
· Side cutting pliers
· Combination pliers
· Personal protective equipment

- gloves

- goggles

Procedure


1. Prepare the necessary tools, materials and equipment.

2. Wear the appropriate PPE.

3. Turn-off power to the circuit. If the voltage source is connected to the circuit during this test, you will damage the meter.
[image: image15.png]& a insulation resistance test. pdf - Adobe Reader
Fie Edt Vew Document Tods Window Help

H & e ee= i @

& proof 1961 can be petformed 08 [0t the manufacturer's b tested.

* test voltages) used for testing o
on 22\1[?222(“%1 {any capaci- o onag qupmem or testing Press the test button to apply
single voltage, usually between 1 Table 1.

NSRS l soiog St 00Tt Vg Prmmintood |
e R AR il Foiaing Exuipment IO Tot olages Formul Used

the insulation Above nomnal Buctory A Tet VA [yl rfetence) | 2. (VAC Nmeplate Rating + 1000
working voltages in order to Masimum DC stallaton Tes, VDG 128 (Patory AC Test

detect subtle weaknesses in the | Masmm D AterService T, U | 0.6 x Fasory &G Ty

insulation. For new equipment,  fabie 1. Proot testvatage equations for rotating machines
the test should be done at about
60% to 80% of the manu-

Metal Conduit

[= teno @ I E [ o



[image: image16.jpg]=)\




4. Select “resistance” on your multimeter (choose the lowest setting). If  using an analog, you must first “zero” the meter by touching the test pros together and turning the thumbwheel until the needle set at zero.

5. Touch the probe tips across the component or portion of the circuit for which you want to determine continuity.
6. Read the meter. (Note: If the reading is low, it means you have continuity(the circuit is closed. If the reading is “infinity’, it means there is no continuity (the circuit is open)

7. Record the data you have gathered.

8. Perform good housekeeping.
Safety precautions

1. Do not attempt to adjust, test or make a repair if you do not have basic repair skills or if you do not fully understand the directions. 
2. Always practice proper and reasonable safeguards as well as those suggested by the manufacturer of the devices and tools you use.
Assessment Criteria
	WORKMANSHIP 
	5 pts.

	ACCURACY OF TESTING
	4 pts.

	USE OF TOOLS AND INSTRUMENTS
	3 pts.

	USE OF PPE
	3 pts.

	SPEED
	3 pts.

	HOUSEKEEPING
	2 pts.

	TOTAL
	20 pts.


operation Sheet 2.2
tracing a short circuit or overload
Tools and Equipment

· Laboratory circuit board
· Multitester
· Screwdriver
· Side cutting pliers
· Combination pliers
· Personal protective equipment

- gloves

- goggles

Procedure

1. Prepare tools, materials and equipment needed.  
2. Wear appropriate PPE.

3. Turn off all wall switches and unplug all lights and appliances.

4. Reset the circuit breaker. Pull the lever to off and then to on again to reset a circuit breaker with a lever switch. If a fuse is blown, it must be replaced. Unscrew the fuse to replace it with one with exactly the same amperage rating (both circuit breakers and fuses should be sized according to the wire used in the circuit they protect).
· Note the following symptoms after resetting the breaker

[image: image17.png]



· If the breaker trips immediately: the problem may be a short circuit in a receptacle or switch. 

· If the breaker does not trip again, turn on each switch one at a time and check if and when the breaker trips again. 

· [image: image18.emf]If turning on a switch causes the breaker to trip, there is a short circuit in a fixture or receptacle controlled by the switch. 

· If turning on the switch makes no difference, the problem is in one of the appliances connected to the switch.

· If the circuit went dead when you plugged in the appliance, the problem is probably in the cord or plug. 

· If the circuit went dead when you turned on the appliance, the appliance itself is defective
5. Mark devices, appliances or circuit with damage. Separate them if possible.
6. Report to the owner/occupant the test that you have done.
7. Perform good housekeeping.
Caution
· To protect yourself, think “Safety First”.
· Use appropriate personal protective equipment such as safety glasses, face shields, insulating gloves, insulating boots, and/or insulating mats.

· Never ground yourself when taking electrical measurements.

· Always work with a partner.

Assessment Criteria

	WORKMANSHIP 
	5 pts.

	ACCURACY OF TESTING
	4 pts.

	USE OF TOOLS AND INSTRUMENTS
	3 pts.

	USE OF PPE
	3 pts.

	SPEED
	3 pts.

	HOUSEKEEPING
	2 pts.

	TOTAL
	20 pts.


operation Sheet 2.3
testing the insulation resistance
Tools and Equipment

· Laboratory circuit board
· Insulation resistance tester
· Screwdriver
· Side cutting pliers
· Combination pliers
· Personal protective equipment

- gloves and goggles

Procedure
1. Prepare all tools, materials and equipment needed.

2. Wear appropriate PPE.
3. Use a multimeter or the voltage measurement function on the MegOhmMeter to make sure there is no power applied to the tested circuit.

4. Select the appropriate voltage level.

5. Plug one end of the black test lead to the common terminal on the meter and touch the test probe to a ground (earth)or another conductor. Sometimes it is helpful to ground all conductors that are not part of the test. Alligator clips can make measurements easier and more accurate.

6. Plug one end of the red test lead to the volt/ohm terminal on the meter and connect the test probe to the conductor to be tested.

7. Press the test button to apply the desired voltage and read the resistance displayed on the meter. It could take a few seconds for the reading to settle. The higher the resistance is the better.
8. Test each conductor against ground and against all the other conductors present in the conduit. Keep a dated record of the measured values in a safe place.

9. If some of the conductors show low resistance, identify the problem or re-pull the conductors. Moisture, water, or dirt can create low resistance readings.

[image: image19.png]o earth resistanc

est. pdf - Adobe Reader

View Documert Tools Window Help

D [1]is  ©® [1ow |- it

#61-796

I,

Earth Ground Resistance Tester
Instruction Manual

796 FEATURES

« Meastres grourd o resistance using 3-poles
o Meastres eath vologe

Do nottrip ground auk breaersinthe
cirut ncer st

Inchudes tetleads and letroces

00 adustnert

Data ol

Lowbatery indicator

/A Read First: Safety Information
Ucstand and ollow perating nstctions arflly I his st s o used na manner
pecied by DEAL poleaion proided by e product may b inpaied

A\ waBNiNG

o acidpossble s shck prsoa iy or dsh, ol s s

" Do not s st appars damage, Vsl e teestr o ensre acs s ot
ctckd and ik s Sy n plc.

o gt o s | nuion s G, el s sgusd, o prbs s
ctckad. Pyl tbnionto s nuonsuounding e ot
A shook it g nomalsing 53 vlage s presearss e messing
i
G0 ot 5ottt apett kol s et eyt g
Do notsedug sl soms o i et vt
Do ot ssaround o g, s, o vapor,
Donotus bteon ez s
oo us it h iy and h ack s propaly sl
Fepce Gty 25 son 25 Us o bty it * £ ppets o vl
wedings
Femove e s s o un pior o ooyt cap
sk th e tminls,nclon and g ot yot strsmens
Do o aenpt o g ik e ho - svicsbl s,
Gomply i ol and eonel sty rments, g te se o spropite
sl prtctvesqipment

CAUTION

To protctyoursel, ik “Sfey Fist”

 Vollages xceeing 30VAC or BVDE posea shock hazad so use cauton.

 Use appropritepersorl protective quipment such s sty glasses s hieds,
insulting olovs, insulting boos, andor nsulating s

N round yoursef when taking slctical measuements

o Always work witha parter

o When using the probes, ke fnges s far behin e probe i s pssible,

Operatng Instrucions N
" Belote prooseding wih ser Figure 1
mesuremen, il he
syminl appears on

hedipla,eplac with

bateris.

Short e tps o te ads. e

Adiustthe 00. ADJ contolto ="

st eading b 260

ol thefunclion swich o s “EARTH VOLTAGE' psionand prssto st Eath vol-

a0 will s dislayed o the LCD. f ath volageis more im0V, an s eading

1 b obained.

Pecision et esisnca measurement ethod

(1) Conne the reen, yellowand e et s o st il €, Pand C with
iyt pes P11t ro bl 1A STRAGHT LI Py 1

@) Robtthe funcion swich o sutable rangs e prss he pushbuton to tectand
ks hereacing

Sinplifedsth essans st method

() This method i tecommended where a rh resistancs ighe than 1022 is
st orwhee s ot possil s rive iy cathspke. An apprsints
vale of gt tesistance an b obined by th b wire systemshown i Fig. 2.

@) Robt the funcion swich o "EARTH VOLTAGE” psiion and pess o st ks
cetan et art volage i s ten 101

(@) Fist ot the function swch o he 2000 psion and press b tst.Readsath
vesistance. th display shows 1 (MSD),swch o th K0 psionand read
cath sistace,

) Th eading obtained () i an Figure 2
aproxinas et esisance

v, Thet s o i for =HET
exermal shoting as P and G / /7 L)

teminalsars shoredty /[ / Kizzza -
usig e ts ads

specifed for thesimplfied =
measuement,

05! 5% 2





[image: image20.jpg]



[image: image21.jpg]



Precautions 
Adhere to the following four-step process before every test: 
· Take the equipment out of service
· Check what will be included in the test
· Discharge capacitance
· Check current leakage at switches
Assessment Criteria

	Workmanship
	6 pts.

	Accuracy of Testing
	4 pts.

	Use of Tools and Instruments
	4 pts.

	Use of PPE
	3 pts.

	Housekeeping
	3 pts.

	TOTAL
	20 pts.


operation Sheet 2.4
measuring voltage in a circuit
Tools and Equipment

· Laboratory circuit board
· Multitester
· Screwdriver
· Side cutting pliers
· Combination pliers
· Personal protective equipment

- gloves

- goggles

Procedure

1. Prepare the necessary tools, materials and equipment needed.
2. Wear the appropriate PPE.
3. Set the meter to the appropriate range for the voltage you expect to find. (Note; When measuring an unknown voltage, select the highest range and workdown.)


4. Touch the negative probe to a known ground and touch the positive lead to the wire you are testing.
5. View the reading on the display and record it.
6. Perform good housekeeping.

Safety precautions

· Always wear eye protection and protective clothing or gear, as appropriate.

· Do not work alone - in the event of an emergency another person's presence may be essential.

· Always keep one hand in your pocket when anywhere around a powered line connected or high voltage system.

Assessment Criteria

	Workmanship
	5 pts.

	Accuracy of Testing
	4 pts.

	Use of Tools and Instruments
	3 pts.

	Use of PPE
	3 pts.

	Speed
	3 pts.

	Housekeeping
	2 pts.

	TOTAL
	20 pts.


operation Sheet 2.5
TESTING THE EARTH RESISTANCE
Tools and Equipment

· Laboratory circuit board
· Earth resistance tester
· Screwdriver
· Side cutting pliers
· Combination pliers
· Personal protective equipment

- gloves

- goggles

Procedure
1. Prepare tools, materials and equipment needed.    
2. Wear appropriate PPE

3. Before proceeding with measurement, if the “ “ symbol appears on the display, replace with new batteries.

4. Short the tips of the leads. Adjust the 0Ω ADJ control to set the reading to zero.

5. Rotate the function switch to the “EARTH VOLTAGE” position and press to test. Earth voltage will be displayed on the LCD. If earth voltage is more than 10V, an inaccurate reading may be obtained.

6. Precision earth resistance measurement method:

· Connect the green, yellow and red test leads to instrument terminals E, P and C with auxiliary earth spikes P1, C1 placed into the soil “IN A STRAIGHT LINE”. (Fig. 1)

· Rotate the function switch to a suitable range then press the push button to test and take the reading.

· Simplified earth resistance measurement method:

· This method is recommended where an earth resistance higher than 10Ω is measured or where it is not possible to drive auxiliary earth spikes. An approximate value of earth resistance can be obtained by the two wire system shown in Fig. 2.

· Rotate the function switch to “EARTH VOLTAGE” position and press to test. Make certain that earth voltage is less than 10V.

· First rotate the function switch to the “200Ω position and press to test. Read earth resistance. If the display shows “1”, switch to the “2KΩ” position and read earth resistance.

· The reading obtained (Rx) is an approximate earth resistance value.

· There is no need for external shorting as P and C terminals are shorted by using the test leads specified for the simplified measurement.

7. Record the data you have gathered.

8. Perform good housekeeping.



Caution

To protect yourself, think “Safety First”.
· Voltages exceeding 30VAC or 60VDC pose a shock hazard so use caution.

· Use appropriate personal protective equipment such as safety glasses, face shields, insulating gloves, insulating boots, and/or insulating mats.

· Never ground yourself when taking electrical measurements.

· Always work with a partner.
· When using the probes, keep fingers as far behind the probe tips as possible.
Assessment Criteria

	Workmanship
	5 pts.

	Accuracy of Testing
	4 pts.

	Use of Tools and Equipments
	3 pts.

	Use of PPE
	3 pts.

	Speed
	3 pts.

	Housekeeping
	2 pts.

	TOTAL
	20 pts.


operation Sheet 2.6
testing phase sequence
Tools and Equipment

· Laboratory circuit board
· Phase sequence tester
· Screwdriver
· Side cutting pliers
· Combination pliers
· Personal protective equipment

- gloves

- goggles

Procedure
1. Prepare tools, materials and equipment needed. 
2. Wear appropriate PPE.
3. Connect the tester to the circuit under test.
4. Check for voltage on all phases: three LEDs marked “A”, “B” & “C” should be on. If there is a lack of voltage on one of the test leads the corresponding LED will not illuminate. If a voltage is present on one or two leads and the remaining leads are connected to neutral or ground, both or all LEDs will illuminate not including the phase sequence LEDs.
5. If the voltages of all phases are correct it is possible to read out the phases’ order by observing the illumination of the LED marked as “NORMAL (ABC)” or “REVERSE”.
6. After conducting a test, the instrument should be disconnected from the circuit under test. The tester left under voltage for long periods of time can overheat. In such a case the built-in thermal protection will disconnect the electronic system and the indications will be switched off. If such a situation occurs, you should disconnect the tester from the installation and wait a few minutes before another use of the tester (the tester will run automatically after cooling down).

7. Record the data you have gathered.
8. Perform good housekeeping.


Caution

Do not test any circuits in the extremely humid or wet environment.
· After transferring the tester from a cold place into a warm one, please, wait about 30 min. to get the tester acclimated to the present conditions. You can wipe the condensed dew, if necessary.

· Do not operate the meter in the environment with explosive gas (material), combustible gas (material), steam or filled with dust.

· Insulate yourself from the objects being measured.

· Do not make contact with any exposed metal (conductive) parts such as the tips of the test leads, sockets, fixing objects, circuits, etc.

· Do not conduct any measurements if the tester is defective, with the defective casing or test leads (breakages, deformations, fractures, contaminations, etc).

Assessment Criteria

	Workmanship
	5 pts.

	Accuracy of Testing
	4 pts.

	Use of Tools and Instruments
	3 pts.

	Use of PPE
	3 pts.

	Speed
	3 pts.

	Housekeeping
	2 pts.

	TOTAL
	20 pts.


	Program/Course:
	BUILDING WIRING INSTALLATION NC II

	Unit of Competency:
	commission installed electrical system

	Module Title:
	Commissioning Electrical System


Learning Outcome 3:  Finalize commissioning activities
Assessment Criteria
	1. Defects are remedied or repaired following prescribed procedure.

	2. Work reports are prepared in line with established policies.

	3. Workplace is cleaned up and made safe in line with established policies.

	4. Tools, equipment and surplus materials are cleaned, checked and stored in line with established procedure.

	5. Final testing is undertaken in line with established procedures.


References:
1. Institute of Integrated Electrical Engineers of the Philippines Incorporated. Philippine Electrical Code of 1992.
2. Max B. Fajardo Jr. & Leo R. Fajardo.  Electrical Layout and Estimate, 2nd Edition.

3. Azares, Efren F. and Recana, Cirilo B.  Practical Electricity III; Adriana Publishing: 1999.

4. Roland E. Palmquist.  Audel House Wiring, 7th Edition.

5. www.des.od.nih.gov/eWebb/…/commissioning/nih_cxguide/cxspecs/1699555k
6. www.epa.gov/rtp/new-bldg/environmental/0910updf
7. www.megger.com/au/products
8. www.omnicontrols.com/manufacturer.megger.aspx

9. www.amprove.com/manuals/PRMZ-pdf

10. www.wikihow.com/use-a-multimeter

11. www.acmehowto.com/howto/maintenance/electrical/onthevoltage.htm
	LEARNING EXPERIENCES/ACTIVITIES



	Learning Outcome 3:  Finalize commissioning activities

	Learning Activities
	Special Instructions 

	2. Read the attached Information Sheet 2.1 on the:
· things to consider in final testing of electrical circuit

· accountability in declaring system as commissioned.

· final activities in commissioning process.
	· You can ask the assistance of your teacher to show you and explain further topics you cannot understand.


	3. Answer Self-Check 2.1 to test your knowledge on the things to consider in final testing of electrical circuit.
	

	4. Compare your answer to answer key 2.1.
	

	5. Answer Activity Sheet 2.1 on Commissioning Grounded Fluorescent and Fixture

	


Information Sheet 3.1
Things to consider in final commissioning activities
In electrical system, there are several electrical circuit defects to be considered.  These include an open circuit, short circuit and grounded circuit.  These factors should be considered in the final testing of the electrical components/circuits.  Remember that the purpose of electric systems commissioning is to increase the reliability of electric power system after installation by identifying problems and providing a et of baseline values for comparison with subsequent routine tests.  A procedure should be developed in the form of commissioning plan.
COMMISSIONING PLAN

Procedures

1. Verify the installation of all equipment/components.

2. Understand the equipment moods of operation.
3. Test the equipment.

Consider the following factors in testing:

· Operation
· Safety requirements

Note: When problems arise during testing of the equipment and system, then troubleshooting techniques should be performed.
Basic Electrical Troubleshooting
1. Gathering information is a logical first step in any troubleshooting endeavor.

Guide questions:

·      What technical documentation about the equipment is available?

· How exactly is the equipment supposed to operate?

2. Understanding the malfunction means that you understand how or what the process is and what portion of the process is operating incorrectly.
Guide questions:

· How is the process supposed to work?

· What is not functioning as it should?

3. Identifying which parameters need to evaluated.

Guide questions:

· How is the process supposed to work?

· What is not functioning as it should?

4. Identifying the source of  the problem requires the technician to

· Isolate components and evaluate circuit parameters.

· Identify the malfunctioning component using the recorded data.

5. Correcting / repairing the component identified as damaged based on the recorded data.

6. Verifying the repair after completion.  Ensure the equipment is operating as designed.

7. Performing root cause analysis.

SELF-CHECK 3.1
Direction: Answer the following questions:
1. In troubleshooting electrical circuit, where are you going to base your repair?
2. What do we need to consider in testing electrical component?
ACTIVITY SHEET 3.1
COMMISSIONING GROUNDED FLUORESCENT FIXTURE

Direction: 
The students will be given a grounded fluorescent fixture.  The teacher will observe them if they have followed the correct procedure in commissioning and also by supplying the needed information written below.  Write your answer on a separate sheet of paper.
Guide question:

1. When was this fluorescent lamp bought?

2. What will happen to the lamp once you turn on the switch?

3. What test instrument is needed?

Table 1
	Symptoms
	Cause
	Remedial Measure

	
	
	


Assessment Plan

	Program/Course:
	BUILDING WIRING INSTALLATION NC II

	Unit of Competency:
	commission installed electrical system

	Module Title:
	Commissioning Electrical System


	Assessment Criteria
	Assessment Methods

	
	Demonstration
	Observation
	Oral Questioning*
	Written Test*
	Work Sample

	LO 1. Perform preliminary activities for commissioning
	
	
	
	
	

	1. Scope of work is confirmed to ensure clear understanding of job elements.
	
	
	
	
	

	2. Planning of commissioning activity is performed in line with work requirements.
	
	
	
	
	

	3. Materials, tools and equipment needed for commissioning are prepared according to work requirements.
	
	
	
	
	

	LO 2. Perform testing of electrical system
	
	
	
	
	

	1. Continuity of circuit is measured following prescribed procedure.
	
	
	
	
	

	2. Insulation resistance is performed following prescribed procedure.
	
	
	
	
	

	3. Supply voltage is measured following prescribed procedure.
	
	
	
	
	

	4. Earth resistance test is performed following prescribed procedure.
	
	
	
	
	

	5. Phase sequence testing is performed following prescribed procedure.
	
	
	
	
	

	LO 3. Finalize commissioning activities
	
	
	
	
	

	1. Defects are remedied or repaired following prescribed procedure.
	
	
	
	
	

	2. Work reports are prepared in line with established policies.
	
	
	
	
	

	3. Workplace is cleaned and made safe in line with established policies.
	
	
	
	
	

	4. Tools, equipment and surplus materials are cleaned, checked and stored in line with established procedure.
	
	
	
	
	

	5. Final testing is undertaken in line with established procedures.
	
	
	
	
	


Observation Checklist

	Student’s name:
	

	Teacher’s name:
	

	Name of School:
	

	Competency standards
	

	Unit of competency:
	

	Instructions for the assessor:

	1. Observe the student [insert description of activity being observed].
2. Describe the assessment activity and the date on which it was undertaken.

3. Place a tick in the box to show that the student completed each aspect of the activity to the standard expected in the enterprise.

4. Complete the feedback sections of the form.

	Date of observation
	

	Description of assessment activity
	

	Location of assessment activity
	

	The student….
	If yes, tick the box

	· can 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	Did the student’s overall performance meet the standard?
	Yes
	No

	Feedback to student:

	Teacher’s signature:
	Date:


Observation and Questioning Checklist

	Student’s name:
	

	Teacher’s name:
	

	Name of School:
	

	Competency standards
	

	Unit of competency:
	

	Instructions for the teacher:

	1. Observe the student [insert description of activity being observed].
2. Describe the assessment activity and the date on which it was undertaken.

3. Place a tick in the box to show that the student completed each aspect of the activity to the standard expected in the enterprise.

4. Ask the student a selection of the questions from the attached list to confirm his/her underpinning knowledge

5. Place a tick in the box to show that the student answered the questions correctly.

6. Complete the feedback sections of the form.

	Date of observation
	

	Description of assessment activity
	

	Location of assessment activity
	

	The student….
	If yes, tick the box

	· can
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	Did the student’s overall performance meet the standard?
	Yes
	No


Demonstration

	Student’s name:
	

	Teacher’s name:
	

	Unit of competency:
	

	Competency standards: 
	

	Date of assessment:
	

	Time of assessment:
	

	Instructions for demonstration

	Given the necessary materials the student must be able to:



	Materials and equipment:



	
	( to show if evidence is demonstrated

	During the demonstration of skills, did the student:
	Yes
	No
	N/A

	
	(
	(
	(

	
	(
	(
	(

	
	(
	(
	(

	
	(
	(
	(

	The student’s demonstration was:


Satisfactory 
(



Not Satisfactory
(


Written report

	Student’s name:
	

	Teacher’s name:
	

	Name of School:
	

	Competency standards
	

	Unit of competency:
	

	Task:

	Your task is to:

· [insert description of task]


	Submission date:
	

	Use the checklist below as a basis for judging whether the student’s report meets the required competency standards.

	The student’s report….
	If yes, tick the box

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	· 
	

	Overall did the student’s report meet the standard?
	Yes
	No

	Comments:



	Student’s signature:
	
	Date:
	

	Teacher’s signature:
	
	Date:
	


PERFORMANCE TEST

	Student's Name
	Date

	Competency:                  
	
Test Attempt

 1st       2nd       3rd


	Directions:
                     

CALL TEACHER, ask teacher to assess your performance in the following critical task and performance criteria below

You will be rated based on the overall evaluation on the right side.


	
OVERALL EVALUATION

	
	Level

Achieved
	
PERFORMANCE LEVELS

	
	
	4 - Can perform this skill without supervision and with initiative and adaptability to problem situations.

	
	
	3 - Can perform this skill satisfactorily without assistance or supervision.

	
	
	2 - Can perform this skill satisfactorily but requires some assistance and/or supervision.

	
	
	1 - Can perform parts of this skill satisfactorily, but requires considerable assistance and/or supervision.

	
	Teacher will initial level achieved.


	
PERFORMANCE STANDARDS

For acceptable achievement, all items should receive a "Yes" or "N/A" response.
	
Yes
	
No
	N/A

	Get from Performance criteria of the module 
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	

	
	
	
	


ANSWER KEY 1.1
A.  Direction: Enumerate the following
1-12.   
Scope of commissioning electrical system
1. Secondary Service Electrical Systems 

2. Motor Control Centers 

3. Distribution and Branch circuit panelboards 

4. Lighting Fixtures and Controls 

5. Lightning Protection Equipment and Lightning Protection Systems 

6. Equipment Monitoring 

7. Fire Alarm Equipment/Fire Alarm Equipment Monitoring System 

8. AC motors 

9. Grounding Equipment and Building Grounding System 

10. Security System 

11. Emergency Generators and Distribution System 

12. Uninterruptible Power Systems
13-18. Work included in commissioning process
13. Systems and equipment testing and start-up. 

14. Validation of proper and thorough installation of Division 16 systems and equipment 

15. Equipment performance verification. 

16. Functional testing of electrical systems.

17. Documentation of tests, procedures, and installations. 

18. Coordination of training
B.  Direction: Identify the word or words being referred to by the statement, write the answer on your answer sheet.
	High potential tester
	1. It is a device used to verify the electrical insulation in a cable, printed circuit board, electric motor, transformer or other wired assembly.

	
	2. 

	Phase sequence tester
	3. It is used to assure proper and safe connection of the electrical equipment on three-phase systems.

	
	4. 

	Megger
	5. It is an instrument used to measure the insulation resistance of conductors or wire.

	
	6. 

	Multitester
	7. It is used to measure either, the voltage, the resistance or the current of a circuit.

	
	8. 


ANSWER KEY 3.1
Direction: Answer the following questions:
1. In troubleshooting electrical circuit, where are you going to base your repair?

2. Recorded date
3. What do we need to consider in testing electrical component?
Operation of the component and safety requirements

































cueto





Unit of Competency:  commission installed electrical system�
�
Module No.: 4�
Module Title: commissioning electrical system�
�






Figure 6. Actual testing of phase sequence





Figure 5. Phase sequence tester























Republic of the Philippines


Department of Education





PUBLIC TECHNICAL-VOCATIONAL 


HIGH SCHOOLS





mhar








Figure 4 (right). Earth resistance tester lead terminal





Figure 3 (above). Earth resistance tester





Figure 2. Actual testing of insulation resistance





Figure 1. How to test conductor resistance




















1

1

